T.W.T  RS485

Controller_MODBUS-RTU Protocol Description

Version: V1.3

Data in this protocol includes: Hexadecimal numbers, Integers, BCD codes, and Floating-point numbers.

For the register addresses listed in the following table, the "Attribute" indicates the read/write permission:

• R: Read-only

• W: Write-only

• R/W: Readable and writable

400W Inverter_MODBUS-RTU Protocol Data Description

| Attribute | Address (hex/word) | Register Length (word) | Data Type | Description | Note (Example) |
| --- | --- | --- | --- | --- | --- |
| (Acquisition Data Information) |  |  |  |  |  |
| R | 0 | 2 | UINT | Display panel firmware version number | --- |
| R | 1 | 2 | UINT | Power drive board firmware version number | --- |
| R/W | 2 | 2 | UINT | Frequency (Speed setting and feedback) | 500/10=50.0Hz |
| R/W | 3 | 2 | UINT | Start/Stop command and operating status feedback | 1: Forward Run2: Stop5: Reverse Run |
| R | 4 | 2 | --- | --- | Reserved |
| R | 5 | 2 | --- | --- | Reserved |
| R | 6 | 2 | --- | --- | Reserved |
| R | 7 | 2 | --- | --- | Reserved |
| R | 8 | 2 | UINT | DC bus voltage value (V) | 3100/10=310.0V |
| R | 9 | 2 | UINT | DC bus current value (A) | 132/100=1.32A |
| R | 10 | 2 | UINT | Heatsink temperature (°C) | 43=43°C |
| R | 11 | 2 | UINT | --- | Reserved |
| R | 12 | 2 | UINT | --- | Reserved |
| R | 13 | 2 | UINT | --- | Reserved |
| R | 14 | 2 | UINT | --- | Reserved |
| R | 15 | 2 | UINT | --- | Reserved |
| R | 16 | 1 | UINT | --- | Reserved |
| R | 17 | 1 | UINT | --- | Reserved |

1. Data Format Description

1.1. Communication Mode

This instrument adopts the MODBUS RTU format.

The protocol uses a master-slave query/response model for data communication. The communication flow is shown in the figure below.

As for RTU format, the figure below

1.2 Data Format

Supported serial port data formats:

• 8N1: 1 start bit, 8 data bits, no parity, 1 stop bit

• 8N2: 1 start bit, 8 data bits, no parity, 2 stop bits

• 8E1: 1 start bit, 8 data bits, even parity, 1 stop bit

• 8O1: 1 start bit, 8 data bits, odd parity, 1 stop bit

Supported baud rates (5 options):

• 2400 (abbreviated as 24), 4800 (48), 9600 (96), 19200 (192), 38400 (384)

Similarly, if a new message begins earlier than 3.5 character times following a previous message, the receiving device will consider it a continuation of the previous message. This will trigger an error, as the CRC checksum will be invalid for the combined messages. A typical message frame is structured as follows:

Where: T1, T2, T3, T4 represent the inter-frame time intervals. The transmission between two frames must exceed this interval time.

1.3 Device Address

(Note: The full content of this section is not visible in the provided image.)

The protocol defines instrument addresses as 01–249 (decimal). Address 0 is reserved for broadcast messages, which this protocol does not support. All other addresses are reserved for future use.

2. MODBUS RTU Command Format Description

2.1 Supported MODBUS Commands

| Command Code (HEX) | Function | Notes |
| --- | --- | --- |
| 3 | Read single or multiple registers |  |
| 6 | Write single register | This command is included in the "Command" set |

2.2 Data Format

Data types supported in this protocol include:

• Hexadecimal numbers

• Integers

• BCD codes

• Floating-point numbers

For register addresses listed in subsequent tables:

• R: Read-only

• W: Write-only

• R/W: Readable and writable

MODBUS Response Frame0

| Field | Size | Range/Value |
| --- | --- | --- |
| Device Address | 1 BYTE | 01–249 |
| Function Code | 1 BYTE | 0x03 |
| Starting Address | 2 BYTE | 0x00–0xFFFF |
| Read Quantity | 2 BYTE | 0x01–0x7D |
| CRC Low Byte | 1 BYTE | Calculated checksum |
| CRC High Byte | 1 BYTE | Calculated checksum |

Modbus Response Frame

| Field | Size | Range/Value |
| --- | --- | --- |
| Device Address | 1 BYTE | 01–249 |
| Function Code | 1 BYTE | 0x03 |
| Byte Count | 1 BYTE | N (number of data bytes) |
| Input Data | 2×N BYTE | Register values |
| CRC Low Byte | 1 BYTE | Calculated checksum |
| CRC High Byte | 1 BYTE | Calculated checksum |

Example (Read Command)

| Request |  |  | Response |  |
| --- | --- | --- | --- | --- |
| Field Name | Data (HEX) |  | Field Name | Data (HEX) |
| Device Address | 1 |  | Device Address | 1 |
| Function Code | 3 |  | Function Code | 3 |
| Starting Address High | 0 |  | Byte Count | 6 |
| Starting Address Low | 6B (108) |  | Register 1 High | 2 |
| Read Quantity High | 0 |  | Register 1 Low | 2B (109) |
| Read Quantity Low | 3 |  | Register 2 High | 0 |
|  |  |  | Register 2 Low | 0 |
|  |  |  | Register 3 High | 0 |
|  |  |  | Register 3 Low | 64 (100) |
| CRC Checksum | (Check code) |  | CRC Checksum | (Check code) |

Command 06 (HEX): Write Single Register Command

MODBUS Request Frame

| Field | Size | Range/Value |
| --- | --- | --- |
| Device Address | 1 BYTE | 01–249 |
| Function Code | 1 BYTE | 0x06 |
| Register Address | 2 BYTE | 0x00–0xFFFF |
| Register Data | 2 BYTE | 0x00–0xFFFF |
| CRC Low Byte | 1 BYTE | Calculated checksum |
| CRC High Byte | 1 BYTE | Calculated checksum |

MODBUS Response Frame (Echoes the request if successful)

| Field | Size | Range/Value |
| --- | --- | --- |
| Device Address | 1 BYTE | 01–249 |
| Function Code | 1 BYTE | 0x06 |
| Register Address | 2 BYTE | 0x00–0xFFFF |
| Register Data | 2 BYTE | 0x00–0xFFFF |
| CRC Low Byte | 1 BYTE | Calculated checksum |
| CRC High Byte | 1 BYTE | Calculated checksum |

Example

| Request |  |  | Response |  |
| --- | --- | --- | --- | --- |
| Field Name | Data (hex) |  | Field Name | Data (hex) |
| Slave Address | 1 |  | Slave Address | 1 |
| Function Code | 6 |  | Function Code | 6 |
| Register Address (High) | 0 |  | Starting Address (High Byte) | 0 |
| Register Address (Low) | 6B |  | Starting Address (Low Byte) | 6B |
| Register Value (High) | 0 |  | Register Value (High) | 0 |
| Register Value (Low) | 0F |  | Register Value (Low) | 0F |
| CRC Checksum | Check code |  | CRC Checksum | Check code |